Supplementary Material for Manuscript FEM‑2026‑0130

Title: Proactive Resilience of Urban Water Supply Cyber‑Physical Systems under Extreme Water Network Malfunctions: An Early Warning Perspective

Journal: ENGINEERING Management

This file corresponds to Supplementary Table S1, the complete table of idealized modeling assumptions, practical impacts, and engineering mitigation options referenced by Section 2.5 of the main manuscript. The main text retains a dedicated “Model Assumptions” section that discusses the three assumptions most relevant to the reported results; the full per‑assumption detail is provided here to keep the main text concise.

Supplementary Table S1. Idealized modeling assumptions, practical impacts, and engineering mitigation options.

|  | Domain | Idealized assumption | Practical impact | Engineering mitigation |
| --- | --- | --- | --- | --- |
| A1 | Temporal resolution | Sensing and control act on the 300 s step; event times are recorded at step boundaries. | Sub‑step dynamics below 5 min are unresolved. For example, the two tanks isolate within the same step, and sub‑step interpolation gives a stagger of 1.6 to 2.6 min. | Finer SCADA polling or event‑triggered reporting. |
| A2 | Pressure aggregation | Nodal gauge pressures below zero, which arise at zero‑demand junctions in a drained network under PDA, are clipped at zero in the network average. | The average pressure is slightly conservative during deep degradation. | Reporting of per‑junction statistics, as in the nodal pressure maps (Figs. 3(c) and 4(d)). |
| A3 | Cyber sensing | Error‑free and continuous telemetry of tank levels and pump states. | Measurement noise or drift could shift trigger times by minutes. | Local Kalman filtering and redundant sensing at tanks. |
| A4 | Communication | Zero latency and no packet loss between SCADA and PLCs. | Delayed curtailment commands on the order of seconds to minutes. | Edge‑computing PLCs with autonomous threshold evaluation. |
| A5 | Control execution | Curtailment is applied instantaneously and uniformly at all junctions. | Real valve and meter actuation requires finite time, and uniform shedding ignores user heterogeneity. | AMI‑enabled smart meters and pressure‑reducing valves with preset emergency routines; priority grading through wj. |
| A6 | Value weighting | Service value is weighted by the normalized demand pattern α(t) rather than by economic loss functions. | The value ranking follows system‑wide demand blocks rather than user‑specific criticality. | Socioeconomic weighting schemes in wj. |
| A7 | Storage anchor | S counts tank storage only; pipe volume is excluded from the value ceiling. | The ceiling slightly understates the available water, and Rw is slightly conservative. | Extension of the anchor with pipe storage estimation. |
| A8 | Hydraulic symmetry | T1 and T2 share identical settings and exhibit equalized drawdown through the looped network. | Site‑specific asymmetries would stagger the two isolations. | Network‑specific calibration and per‑tank reporting, as in Figs. 4(b) and 4(c). |
| A9 | Disturbance | Deterministic step‑function total outage of 24 to 48 h. | Real outages may be partial or cascading. | Multi‑factor scans, including durations of 12 to 48 h (Section 3.4). |
| A10 | Water quality | No water quality deterioration, such as chlorine decay or water age increase, during emergency supply. | Low velocities under curtailment may increase stagnation. | Limitation of the CRITICAL state duration and post‑event flushing. |
| A11 | Pump control | Pumps are binary (on or off) without variable speed operation. | Variable‑frequency‑drive‑based pressure management is not explored. | Extension of the action set with pump speed modulation. |